Changes in the 2005 National Electric code. As always, have your code book open or your electronic copy ready for complete section references.  Code books are available from your electrical supply stores, sign association and direct from the National Fire Protection Association.  Electronic copies are available on CD and for direct download from the NFPA site at www.nfpa.org. The sections of the code that appear will have sections underlined meaning they are the words that have been added.

# Article 80 Administration and Enforcement

## This section is where the local electrical inspector draws their authority to administer and enforce the code.  This section was moved completely to:  Annex G, and no other changes were made

# Article 90 Introduction

## 90.1 Purpose

## (D) Relation to Other International Standards.

## The requirements in this Code address the fundamental principles of protection for safety contained in Section 131 of International Electrotechnical Commission Standard 60364-1,Electrical Installations of Buildings.

The word other was added to include any additional Standards that may apply.

# Chapter 1 General

# Article 100 Definitions

The following definitions which relate to our industry have been added or changed.

## Authority Having Jurisdiction (AHJ). The organization, office, or individual responsible for approving equipment, materials, an installation, or a procedure.

## The addition of the (AHJ) was included for clarity. (AHJ) was added to fine print note (FPN).  The fine print notes are used for explanation.

Outline Lighting. An arrangement of incandescent lamps, electric discharge lighting, or other electrically powered light sources to outline or call attention to certain features such as the shape of a building or the decoration of a window.

The additional references to electrically powered light sources are for LEDS and other source being brought to market in the sign industry.

Article 110 Requirements for Electrical Installations

### I. General

110.1 Scope. This article covers general requirements for the examination and approval, installation and use, access to and spaces about electrical conductors and equipment; enclosures intended for personnel entry; and tunnel installations.

The statement was added for clarity for spaces designed for personnel entry.

#### Chapter 2 Wiring and Protection

Article 250

Grounding and Bonding

##### The title was changed to include and bonding.

250.2 Definitions.

Effective Ground-Fault Current Path. An intentionally constructed, permanent, low-impedance electrically conductive path designed and intended to carry current under groundfault conditions from the point of a ground fault on a wiring

system to the electrical supply source and that facilitates the operation of the overcurrent protective device or ground fault detectors on high-impedance grounded systems.

250.8 Connection of Grounding and Bonding Equipment.

### Grounding conductors and bonding jumpers shall be connected by exothermic welding, listed pressure connectors, listed clamps, or other listed means. Connection devices or fittings that depend solely on solder shall not be used. Sheet metal screws shall not be used to connect grounding conductors

or connection devices to enclosures.

The words were added for clarity to include connection devices that cannot be connected with sheet metal screws.

250.112 Fastened in Place or Connected by Permanent Wiring Methods

(Fixed) — Specific. Exposed, non–current carrying metal parts of the kinds of equipment described in 250.112(A) through (K), and non–current-carrying metal parts of equipment and enclosures described in 250.112(L) and (M), shall be grounded regardless of voltage.

Marked for change but can find no change:

250.119 Identification of Equipment Grounding Conductors.

Unless required elsewhere in this Code, equipment grounding conductors shall be permitted to be bare, covered, or insulated. Individually covered or insulated

equipment grounding conductors shall have a continuous outer finish that is either green or green with one or more yellow stripes except as permitted in this section. Conductors with insulation or individual covering that is green, green with one or more yellow stripes, or otherwise identified as permitted by this section shall not be used for ungrounded or grounded circuit conductors

This wording is added to clarify that (equipment grounding) bonding conductors are different from the (ungrounded) line conductors (grounded) neutral conductors, and shall be marked differently.

#### Article 300

#### Wiring Methods

300.3 Conductors.

(A) Single Conductors. Single conductors specified in Table 310.13 shall only be installed where part of a recognized wiring method of Chapter 3.

Exception: Individual conductors shall be permitted where installed as separate overhead conductors in accordance with 225.6.

Exception was added to clarify the use of single conductors in field installed systems.

### Article 310

#### Conductors for General Wiring

310.5 Minimum Size of Conductors. The minimum size of conductors shall be as shown in Table 310.5, except as permitted elsewhere in this Code.

### Article 600 Modifies this section to allow GTO wire to be used in 18 and 14 AWG for over 1000 volts.

### Article 310

#### Conductors for General Wiring

310.5 Minimum Size of Conductors. The minimum size of conductors shall be as shown in Table 310.5, except as permitted elsewhere in this Code.

### Article 600 Modifies this section to allow GTO to be used in 18 and 14 AWG for over 1000 volts.

310.8  Locations.

(D) Locations Exposed to Direct Sunlight. Insulated conductors or cables used where exposed to direct rays of the sun shall comply with one of the following:

(1) Cables listed, or listed and marked, as being sunlight resistant

(2) Conductors listed, or listed and marked, as being sunlight resistant

(3) Covered with insulating material, such as tape or sleeving, that is listed, or listed and marked, as being sunlight resistant

This section was made into a list and added the covering material sleeving.  This will allow the use of sleeving to protect GTO wire.

###### Article 314

Outlet, Device, Pull and Junction Boxes; Conduit Bodies; Fittings; and Manholes  Handhole Enclosures

The wording was added to change title.

I Scope and General

314.1 Scope. This article covers the installation and use of all boxes and conduit bodies used as outlet, device, junction, or pull boxes, depending on their use, and handhole s and other electrical enclosures. Intended for personal entry Cast, sheet metal, nonmetallic, and other boxes such as FS, FD, and larger boxes are not classified as conduit bodies. This article also includes installation requirements for fittings used to join raceways and to connect raceways and cables to boxes and conduit bodies.

This section was revised to remove the personal entry restriction.

314.29 Boxes, Conduit Bodies, and Handhole Enclosures to Be Accessible. Boxes, conduit bodies, and handhole enclosures shall be installed so that the wiring contained in them can be rendered accessible without removing any part of the building or, in underground circuits, without excavating sidewalks, paving, earth, or other substance that is to be used to establish the finished grade.

Exception: Listed boxes and handhole enclosures shall be

permitted where covered by gravel, light aggregate, or noncohesive

granulated soil if their location is effectively identified

and accessible for excavation.

### This section revised to include handhole enclosures.

Article 356

Liquidtight Flexible Nonmetallic Conduit: Type LFNC

356.12 Uses Not Permitted. LFNC shall not be used as follows:

(1) Where subject to physical damage

(2) Where any combination of ambient and conductor temperatures is in excess of that for which the LFNC is approved

(3) In lengths longer than 1.8 m (6 ft), except as permitted by 356.10(5) or where a longer length is approved as essential for a required degree of flexibility

(4) Where the operating voltage of the contained conductors is in excess of 600 volts, nominal, except as permitted in 600.32(A)

(5) In any hazardous (classified) location other than as permitted

in 501.10(B), 502.10(A) and (B), 503.10(A), and

504.20

Wording added to (4) to clarify reference to article 600 and its ability to modify this section for a specific use in signs.

356.20 Size.

(A) Minimum. LFNC smaller than metric designator 16 (trade

size 1⁄2) shall not be used unless permitted in 356.20(A)(1)

through (A)(3) for metric designator 12 (trade size 3⁄8).

(1) For enclosing the leads of motors as permitted in

430.245(B)

(2) In lengths not exceeding 1.8 m (6 ft ) as part of a listed

assembly for tap connections to luminaires (lighting

fixtures) as required in 410.67(C), or for utilization

equipment

(3) For electric sign conductors in accordance with 600.32(A)

This section was no change, but a reference to signs.

Chapter 4 Equipment for General use

ARTICLE 410

Luminaires (Lighting Fixtures), Lampholders, and Lamps

I. General

410.1 Scope. This article covers luminaires (lighting fixtures), lampholders, pendants, incandescent filament lamps, arc lamps, electric-discharge lamps, decorative lighting products, lighting accessories for temporary seasonal and holiday use, portable flexible lighting products, and the wiring and equipment forming part of such lamps, luminaires (fixtures), products and lighting installations.

The Wording was changed to include other lighting items and products.  This section will now cover decorative and seasonal lighting items.

#### ARTICLE 600

#### Electric Signs and Outline Lighting

600.1 Scope. This article covers the installation of conductors and equipment for electric signs and outline lighting. All installations and equipment using neon tubing, such as signs, decorative elements, skeleton tubing, or art forms, are covered by this article.

Scope statement completely rewritten for clarity based on input from the (TCC) Technical Correlating Committee.

600.2 Definitions.

Section Sign. A sign or outline lighting system, shipped as subassemblies that requires field-installed wiring between the subassemblies to complete the overall sign.

New definition added to try and clarify what a section sign consists of and describes how subassemblies, not a bag of parts, is required for a Listed Section Letter Sign.

600.3 Listing. Electric signs, section signs, and outline lighting — fixed, mobile, or portable — shall be listed and installed in conformance with that listing, unless otherwise approved by special permission.

Section signs was added to the Listing requirement for clarity.  Section letter signs may be Listed when shipped with subassemblies, installation instructions, and marking which indicate the need for field inspection of connections made in the field.

600.8 Enclosures. Live parts, other than lamps, and neon tubing shall be enclosed. Transformers and power supplies provided with an integral enclosure, including a primary and secondary circuit splice enclosure, shall not require an additional enclosure.

The last part of this section was just rewritten from an exception into positive language.

600.12 Field-Installed Secondary Wiring. The field-installed secondary circuit wiring of section signs shall comply with 600.31 if 1000 volts or less, or with 600.32 if over 1000 volts.

This new section was added in an attempt to satisfy the inspection problem with Listed section letter signs.  Currently without access to Part Two the electrical inspector has no guidance on the sections, which require field connection and inspection.  This should also increase the need for sign companies to provide detailed installation instructions to the local electrical inspector.

600.24 Class 2 Power Sources. In addition to the requirements of Article 600, signs and outline lighting systems supplied by Class 2 transformers, power supplies, and power sources shall comply with 725.41.

This section was added to allow for low voltage LED power supplies when used in signs and outdoor lighting applications.

600.31 Neon Secondary-Circuit Conductors, 1000 Volts or Less, Nominal.

(B) Insulation and Size. Conductors shall be listed, insulated, and not smaller than 18 AWG.

Removed Listed for the purpose; The (TCC) Technical Correlating Committee requested the removal of “for the purpose” for consistency throughout the code, but should have been opposed since many of the products used in our industry is Listed but for another purpose.  IE: 600 volt Computer bushing, which is commonly found in our high voltage raceways.

600.32   Neon Secondary Circuit Conductors, Over 1000 Volts, Nominal.

(H) Between Neon Tubing and Midpoint Return. Conductors shall be permitted to run between the ends of neon tubing or to the secondary circuit midpoint return of listed transformers or listed electronic power supplies and provided with terminals or leads at the midpoint.

Removed Listed for the purpose; The (TCC) Technical Correlating Committee requested the removal of “for the purpose” for consistency throughout the code, but should have been opposed since many of the products used in our industry is Listed but for another purpose.  IE: 600 volt Computer bushing, which is commonly found in our high voltage raceways.

600.42  Electrode Connections

(D) Receptacles. Electrode receptacles shall be listed.

(G) Electrode Enclosures. Electrode enclosures shall be listed.

Both sections (D) and (G) removed Listed for the purpose; The (TCC) Technical Correlating Committee requested the removal of “for the purpose” for consistency throughout the code, but should have been opposed since many of the products used in our industry is Listed but for another purpose.  IE: 600 volt Computer bushing, which is commonly found in our high voltage raceways.

III. Class 2 and Class 3 Circuits

725.41 Power Sources for Class 2 and Class 3 Circuits.

(A) Power Source. The power source for a Class 2 or a

Class 3 circuit shall be as specified in 725.41(A)(1), (A)(2),

(A)(3), (A)(4), or (A)(5):

This is a new section added to include Leds and other low voltage equipment.

This concludes the changes relative to signs in the new 2005 addition of the National Electric Code.

Some of the major changes will be that wholesale channel letter manufacturers will not longer be able to send out partially assembled letters with Listing labels, requiring final assembly by sign companies in the field.  If they wish to send the letters with Listing labels they will now need to be assembled complete with subassemblies and furnished with detailed installation instructions for the installer and the local electrical inspector.

Comments and questions can be e-mailed to Randy@ussc.org